Facilities Operations Energy Conservation Checklist

Agency Coordinator:  					Date:

Building Address:						Building ID:

| Building Operations – Energy Saving Opportunities Checklist |
| --- |
| Illumination | Y | N | N/A |
| Exterior Lights On/Off Control On a timer? Photo Cell? Controlled by a Building Automation System Manually operated by personnel Low Cost Energy Conservation Measure(ECM): If the lights are manually operated, install a low cost timer or photo cell. Interior lights On/Off Control Controlled by a Building Automation System Controlled by a mechanical system clock Manually operated by personnel No control No Cost ECM: Identify a person responsible for turning off lights at the end of business hours. Periodical checks must be made to verify. (17% savings of lighting cost) Low Cost ECM: Reduce lighting levels by removing unnecessary fixtures. This could save 15 to 28% of the lighting costs. |  |  |  |
| Building Automation System | Y | N | N/A |
| Building is equipped with an Energy Management System. Host computer? Graphics? Is it the system user friendly? Simple Payback ECM: Installing an automations system to operate HVAC equipment in Buildings with 10,000 ft2 or more can save 10 to 30% energy use. |  |  |  |
| Temperature Set Points | Y | N | N/A |
| Comfort Zone - Set Points Summer range - 75°F to 78°F Winter range - 68°F to 72°F Zone thermostat controls are set within the above ranges Thermostats are locked to prevent tampering No Cost ECM: For each degree of temperature set point raised during the cooling season t typically saves 3% of the cooling cost. No Cost ECM: For each degree of temperature set point lowered during the heating season typically saves 5% of the heating cost. |  | □ | □ |
| Occupancy Schedules | Y | N | N/A |
| HVAC equipment is scheduled to run when the building is occupied only. Building Automation System is fully utilized Start/Stop Optimization program is enabled Systems are scheduled to start early for pre-cooling Occupancy schedules are updated Holiday Schedule is updated and utilized No Cost ECM: Utilize the BAS energy management system programs where applicable. |  |  |  |
| Domestic Water Heaters | Y | N | N/A |
| Gas & Electric water heater temperature set point at 140°F. Set back water heater set point from 140 °F to 110 °F No Cost ECM: Reducing the water temperature will save from 6% to 12% of hot water cost. |  |  |  |
| Elevators | Y | N | N/A |
| Elevator generators and motor automatic shutdown timer. Check with elevator service company if systems are working properly Low Cost ECM: If the elevator system does not have an automatic shutdown timer, have one installed. This will reduce wear on the equipment as well as save energy. |  |  |  |
| Preventive Maintenance Program | Y | N | N/A |
| Preventive Maintenance Program is managed with a computerized database. Work-Order tracking system Preventive Maintenance Corrective Maintenance Routine Maintenance Contractual maintenance Properly maintained equipment saves 15 to 20% of the operating cost. |  |  |  |